## Sheet1
W1.20
Factors to convert NM3to M3 and M3 to NM3
Sr no. | Temp. | Kelvin | Kelvin/273 | altitude | barometric |  | M3 from | NM3 from
| o C |  |  | meters | pressure |  | NM3 | M3
mmwg
| t | K | a = K/273 |  | p | c = | d = | e =
[5 empty] | # | 10335/p | a*c | 1/d
| 0 | 273 | 1 | 0 | 10335 | 1 | 1 | 1
| 200 | 473 | 1.7326 | 50 | 10273.7766 | 1.006 | 1.7429 | 0.57375
| 300 | 573 | 2.0989 | 200 | 10091.866 | 1.0241 | 2.1495 | 0.46523
| 350 | 623 | 2.2821 | 300 | 9972.0478 | 1.0364 | 2.3651 | 0.42281
| K | obtain Kelvin using 'rs 24'
| # | obtain barometric pressure at any altitude using 'rs 25'
when static pr. Is negative, same has to be allowed for to work out actual
barometric pressure.
example
barometric pr. at sea level is 10335 mmwg
altitude at place 300 metres. Barometric pr. at place=9972mmwg
draft in gas system like at entry of fan= -500 mmwg
temp. of gas 350 o c.
|  | gas volume of 1000 nm |  | nm3 would be converted into m3 |  |  | m3 by the following
factor
(kelvin/273)*1033/(9972-500) = 2.49
actual gas volume = 1000 *2.49 = 2490 m3
|  | for converting m3 into nm |  | o nm3 , factor = 1/2.49 = 0.402
2490*0.402=1000
when static pr. Is positive only barometric pressure at site needs to be
taken into account.
inputs
calculated outputs
final
|  | rs 26 | checked
|  |  | corrected |  | 30/12/06 |  | compiled