## Sheet1
W1.31
Air for Combustion
for solid, liquid and gaseous fuels
1 | Theoretical Formula
| A | Solid and liquid fuels |  |  |  | Unit
|  | Lo = (1.867C+5.6H+0.7S-0.7O)/0.210 |  |  |  | nm3 /kg
| B | Gaseous fuel
|  | Lo =( 0.5H2+CO+2CH4+3(C2H4)-(O2))/0.210 |  | 2(CH4)+3(C2H4)-(O2))/0.210
nm3/nm3
where H, C,S and O are % contents of Hydrogen, Carbon, Sulphur and
Oxygen respectively.
2 | Practical Formula
|  | Lo = (a*H1/1000 + b ) |  | for solid and liquid fuels |  | nm3 /kg
|  |  |  | for gaseous fuels |  | nm3/nm3
H1 = useful calorific value of fuel
Lo = theoretical air for combustion in nm3 /kg or nm3 of fuel
a and b are constants
Rosin Felling
|  | Fuel |  |  | a | b
| 1 | Solid | H1 >5000 |  | 1.01 | 0.5
|  |  | H1 <5000 |  | 1.1 | 0
| 2 | Liquid |  |  | 0.85 | 2
| 3 | Gas | high cal.value |  | 1.09 | -0.25
|  |  | low cal. Value |  | 0.875 | 0
3 | Actual air requirement
It is customary to supply air in excess of theoretical quantity mentioned above-
particularly true when fuel is coal. Quantity of excess air depends on quantity
of ash and volatiles in coal and on fineness to which it is ground. Calorific values
of coal also fluctuate. Customarily quantum of excess air is taken as 10 %
| Lv = Lo + Lev |  |  | Lev=excess air
let m = % excess air then actual air supplied = Lo*(1+ m/100)
after combustion excess air moves with products of combustion
Hence gases leaving kiln ( or kiln and calciner ) consist of products of combustion
plus excess air.
Example
|  | fuel | coal | cal. Value kcal/kg
|  | H1 |  | 5000 | 4500 | 4000 | 3800
|  | Lo | nm3 /kg | 5.55 | 4.95 | 4.4 | 4.18
|  | fuel | oil
|  | H1 | 9600 | kcal/kg
|  | Lo | 10.16 | nm3 /kg
Actual air for combustion for different excess air ratios
coal
|  | H1 | 5000 | 4500 | 4000 | 3800
|  | Lo | 5.55 | 4.95 | 4.4 | 4.18
with
excess air
%
|  | 10 | 6.1138 | 5.445 | 4.84 | 4.598
|  | 15 | 6.3917 | 5.6925 | 5.06 | 4.807
|  | 20 | 6.6696 | 5.94 | 5.28 | 5.016
|  | 25 | 6.9475 | 6.1875 | 5.5 | 5.225
inputs
outputs
source : Onoda Manual