## Sheet1
W2.C5
CALCULATING PRESSURE DROP IN A BRANCHED GAS CIRCUIT
pr. loss in a branched circuit with many inlets and one outlet
outlet leading to say a dust collector
sr no | item | symbol | unit | formula | quantity
|  |  |  | ,4 | 5,
|  |  | 3 |  |  | 6,
8,
branched circuit
2,
| v | 7,
1,
|  | V | v | D
|  | m3/sec | m/sec | m | temp | dust burden |  | t | T
[8 empty] | 100 | 373
[8 empty] | 60 | 333
| 1 | 20 | 16 |  | 100 | 100 |  | 91.23 | 364.2309
| 7 | 5 | 18 |  | 60 | 50 |  | 60 | 333
| 2 | 25 | 16 |  | 91 | 89.0608 |  | 82 | 354.5642
| 8 | 10 | 18 |  | 60 | 50 |  | 35.0319
| 3 | 35 | 16 |  | 82 | 77 |  | 38.5
| 4 | 35 | 16 |  | 80 | 77
| 5 | 40 |  |  | 80 |  |  | 77.1292
| 6 | 40 | 16 |  | 75 | 0
real density
| notes: | [7 empty] | 1-2, |  | 0.9775
| altitude |  | m |  |  | 0 |  |  | 7-2, |  | 1.1765
| gas |  |  |  |  | air |  |  | 2-3, |  | 1.099
| material |  |  | raw meal
| density |  |  |  |  | 960 |  | re
density
ofair in various
sections
| 1-2, |  |  |  |  | 0.94416 |  | 1.0062
| 7-2, |  |  |  |  | 1.0576
| 8-3, |  |  |  |  | 1.0576
| 3-4, |  |  |  |  | 1.01
| 4-5, |  |  |  |  | 1
| 5-6, |  |  |  |  | 1
volumes
| 1-2, |  |  |  |  | 14.6381
| 7-2, |  |  |  |  | 4.0991
| 2-3, |  |  |  |  | 18.7372
| 8-3, |  |  |  |  | 8.1982
| 3-4, |  |  |  |  | 26.9354
| 5-6, |  |  |  |  | 29.6289
remps
1-2,
7-2,
2-3,
8-3,
| 2010-03-04 | [5 empty] | 2-3, | 8-3, | 3-4, | 4-5, | 5-6,
5-6,
[5 empty] | 1-2, | 7-2, | 25 | 10 | 35 |  | 38
| gas flow | m3/sec |  |  | 20 | 5 | 18 | 18 | 18 | 0 | 16
| temp. | [5 empty] | 0.8413 | 1.5739 | 1.5739 |  | 1.7395
| velocity | m/sec |  |  | 18 | 18 | 30 | 15 | 10 |  | 15
| duct dia | m |  |  | 1.1898 | 1.3302 | 10 | 10 | 0 | 0 | 0
| length | m |  |  | 20 | 10 | 1 | 0 | 0 |  | 1
| lift | m |  |  | 20 | 9 | 0 | 1 | 0 |  | 0
| bends 90 |  |  |  | 0 | 0 | 90 | 60 | 80 |  | 75
| 60 |  |  |  | 0 | 1
| temp. | o |  |  | 100 | 100
| altitude | m |  |  |  |  | 1.29 | 1.29 | 1.29 | 1.29 | 1.29
| density@ | [5 empty] | 0.97 | 1.06 | 1 | 1 | 1.01
| ntp | kg/m3 |  |  | 1.29 | 1.29 | 178 | 100 | 154 | 0 | 140
| density actual |  |  |  | 0.94 | 1.06
| dust burden | gm/nm3 |  |  | 200 | 100 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14
densitywith
| material | kg/m3 |  |  | 1.14 | 1.22
[7 empty] | 16.5138 | 16.5138 | 16.5138 | 0 | 13.0479
[7 empty] | 18.8257 | 18.8257 | 18.8257 | 0 | 14.8746
| velocity head |  |  |  | 16.5138 | 16.5138
| velocity pr. | mmwg |  |  | 18.8257 | 20.1468
ratio wm/wa
| k factor 90 |  |  | 0.18 |  |  | 13.4399 | 3.592 | 2.3946 | 150 | 2.568
| 60 |  |  | 0.218
| pr. loss |  |  |  | 6.3356 | 3.0322
| friction | mmwg
[7 empty] | 3.3886 | 0 | 0 | 0 | 2.6774
[7 empty] | 0 | 4.104 | 0 | 0 | 0
| pr. loss bends | mmwg |  | 90 | 0 | 0
|  |  |  | 60 | 0 | 4.392 | 0.18 | 0.09 | 0.15 |  | 0.14
| pr. loss lift | mmwg |  |  |  |  | 0.01746 | 0.00954
| wm/wa |  |  |  | 0.21 | 0.09
[5 empty] | 0.00987 | 0.0106
| total pr. loss | mmwg |  |  |  |  | 16.846 | 4.1135 | 2.3946 | 150 | 5.2454
[5 empty] | 6.01 | 4.4026
since points 2 and 3 are junctions, the drafs at these points would be same. For example if draft at
1 is -25mms then draft at 2 along line 1-2 would be -31mm. Pr. drop along line 7-2 should be also
-31 mm. Since pr. drop in line 7-2 is ~4.5 mms, draft at 2 should be - 26.5 mms. The line 7-2 should
have a damper to control the pr. drop in it sothat this condition can be met. Along line 2-3 draft at 3
would be -34.4 mmm. By same logic, draft at 8 should be ~-30 mms. If diferent, a damper would be
| introduced in line 8-3, it should be possible to balance ciruits | [5 empty] | 4-5, | 5-6, |  | total
|  | total pr. drop in circuit including bag filter (item 4-5) would be |  |  |  |  | -200 | -5.25 |  | -205.25
|  |  | 1 | 1-2, | 2-3, | 3-4,
|  | mmwg | -25 | -6 | -17 | -2.39
draft fan with margin could be say 300 mm wg
***

## Sheet2
24/8/10
etc
sr no | item | symbol | unit | equation | 1 | 2 | 3 | 4 | 5 | 6 | 7
[5 empty] | 1-2, | 7-2, | 2-3, | 8-3, | 3-4, | 4-5, | 5-6,
| altitude |  | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| temp. ambient |  | o c | 35 | 100 | 60 | 90 | 60 | 80 | 80 | 75
conveying
| media |  |  | air
| density at ntp |  | kg/m3 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29 | 1.29
| dust conveyed |  |  | raw meal
| density |  | kg/m3 | 960 | 960 | 960 | 960 | 960 | 960 | 960 | 960
| temp.correct |  |  |  | 0.7319 | 0.81982 | 0.75207 | 0.81982 | 0.77337 | 0.77337 | 0.78448
altitude correct | bar: 1 to 7
| total correct |  |  |  | 0.7319 | 0.81982 | 0.75207 | 0.81982 | 0.77337 | 0.77337 | 0.78448
| density at temp. |  | kg/m3 |  | 0.94416 | 1.0576 | 0.97017 | 1.0576 | 0.99765 | 0.99765 | 1.012
| sp. volume |  | m3/kg |  | 1.0591 | 0.94557 | 1.0308 | 0.94557 | 1.0024 | 1.0024 | 0.98816
dust burden
| ingas |  | gm/nm3 |  | 200 | 100 | 178.1217 | 100 | 153.9121 |  | 139.845
| vol actual |  | m3/sec |  | 20 | 5 | 25 | 10 | 35 | 35 | 38
| vol.at ntp |  | nm3 |  | 14.6381 | 4.0991 | 18.8017 | 8.1982 | 27.068 | 27.068 | 29.8103
| density with |  |  |  | 1.14 | 1.2209 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14
| dust load |  | kg/m3
| ratio wm/wa |  |  |  | 0.21183 | 0.094557 | 0.1836 | 0.094557 | 0.15427 | 0 | 0.13819