## Sheet1
W2.C6
Duct balancing in a simple parallel circuit
sr no | item | symbol | unit | formula | quantity
|  |  | V2D2 | n | L2
| a |  |  |  |  | c
m
|  |  | V1D1 |  | L1
|  | p1 |  |  | p2
| case1 |  | volumes and lengths differ
[5 empty] | 1 | 2
| volume | V | m3/sec |  | 20 | 5
| velocity | v | m/se |  | 20 | 18
| diameeter | D | m |  | 1.1287 | 0.59489
| length | L | m |  | 30 | 40
| gas/air |  | air |  | air | air
| temp. |  | oc |  | 100 | 100
| altitude |  | m
| density at ntp |  | kg/m3 |  | 1.29 | 1.29
corrected
| density |  | kg/m3 |  | 0.837 | 0.837
| velocity head |  |  |  | 20.3874 | 16.5138
| velocity pr. |  | mmwg |  | 17.0642 | 13.822
| no 90o bends |  | no |  | 2
| no 60o bends |  | no |  |  | 2
| k factor 90 |  |  |  | 0.21
| k factor 60 |  |  |  |  | 0.218
| friction coeff |  |  |  | 0.02 | 0.02
| pr. loss in duct |  |  |  | 9.071 | 18.5878
| pr. drop in bends |  |  |  | 7.167 | 6.0264
| total |  |  |  | 16.2379 | 24.6142
since two branches meet at points a and c, pressures, drafts
have to be same at these two points and pressure drop in leg
amc has to be the same as leg anc
since nothing much can be done by way of layout of duct except selecting
type of bends, only possible way to equalise pr drop is to increase velocity
in duct 1
or to introduce reistance by way of damper or orifice in duct 1.
let us see if pr. drop in duct 2 can be redued by reducing velocity futrther
pr drop in duct alone should be (16.24-6.03 =~ 10 mm)
required velocity works out to13 m/sec. which is far too low.
therefore only possibility is to introdue resistance in leg 1
***